## Cooler Parameter Input
BBCS2 Cooler Efficiency Calculator
Temperatures (°F)
Cooler # | IC-1 |  | IC-2 |  | IC-3 |  | AC/IC-4 |  |  | Date of Assess
| T_in | T_out | T_in | T_out | T_in | T_out | T_in | T_out |  | 2025-06-26
1 | 179 | 91.5 | 206.9 | 92.4 | 209.6 | 90.6 | 225.3 | 114.9
2 | 178 | 97 | 209.1 | 94.5 | 210.4 | 94.5 | 228.2 | 100.6
3 | 178.2 | 91.6 | 210.8 | 93.2 | 210.3 | 91 | 227 | 116
4 | 177.8 | 91.2 | 210.6 | 89.6 | 209.6 | 89.8 | 233.8 | 114.4
5 | 179.7 | 90.8 | 207.9 | 93 | 206.1 | 91.7 | 228.3 | 116.8
6 | 180.4 | 92.3 | 206 | 91.5 | 206 | 92.8 | 230 | 116.1
7 | 177.6 | 91.5 | 195.1 | 92.9 | 205 | 90 | 218.8 | 114.5
8 | 184 | 93.4 | 208.7 | 94.7 | 209.5 | 92.9 | 227.5 | 115.7
9 | 184 | 97.4 | 215 | 94.8 | 210.3 | 90.9 | 220.2 | 116.2
10 | 186 | 92.8 | 208.65 | 89.3 | 209 | 90.4 | 218 | 115.5
Flows (MMCFD) |  |  |  | T Setpoint (°F) & Louver Position (%)
Cooler # | Inlet Gas Today | Total Flow Today |  | Cooler # | IC-1 |  |  | IC-2 |  |  | IC-3 |  |  | AC/IC-4
1 | 5.8 | - |  |  | T Setpoint | Louver | Actual T | T Setpoint | Louver | Actual T | T Setpoint | Louver | Actual T | T Setpoint | Louver | Actual T
2 | 5.7 | - |  | 1 | - | 81.4% |  | - | 100% |  | - | 62.8% |  | - | 25.6%
3 | 5.6 | - |  | 2 | - | 100% |  | - | 100% |  | - | 100% |  | - | 0%
4 | 5.4 | - |  | 3 | - | 89.8% |  | - | 100% |  | - | 47.8% |  | - | 48.1%
5 | 5.8 | - |  | 4 | - | 100% |  | - | 98.9% |  | - | 99.4% |  | - | 25.5%
6 | 5.8 | - |  | 5 | - | 100% |  | - | 100% |  | - | 75% |  | - | 27.3%
7 | 5.9 | - |  | 6 | - | 79.6% |  | - | 56.3% |  | - | 100% |  | - | 38.6%
8 | 5.7 | - |  | 7 | - | 100% |  | - | 100% |  | - | 64.3% |  | - | 31%
9 | 6.3 | - |  | 8 | - | 100% |  | - | 100% |  | - | 100% |  | - | 31.3%
10 | 6.2 | - |  | 9 | - | 100% |  | - | 100% |  | - | 80.6% |  | - | 17.9%
|  |  |  | 10 | - | 100% |  | - | 51.4% |  | - | 38.5% |  | - | 35.3%
Actual Duty (1000 BTU/hr)
Cooler # | IC-1 |  | IC-2 |  | IC-3 |  | AC/IC-4
| Duty | Efficiency % | Duty | Efficiency % | Duty | Efficiency % | Duty | Efficiency %
1 | 736.1522 | 104.6262 | 963.3078 | 103.8146 | 1001.167 | 106.192 | 928.8138 | 102.1081
2 | 669.7172 | 95.1841 | 947.5258 | 102.1138 | 958.2744 | 101.6424 | 1055.0113 | 115.9815
3 | 703.4569 | 99.9794 | 955.2717 | 102.9486 | 969.0809 | 102.7887 | 901.6595 | 99.1229
4 | 678.3334 | 96.4087 | 947.7869 | 102.1419 | 938.3874 | 99.533 | 935.2542 | 102.8161
5 | 696.3492 | 98.9692 | 900.0059 | 96.9926 | 896.0894 | 95.0466 | 873.3739 | 96.0134
6 | 690.0829 | 98.0786 | 896.8727 | 96.655 | 886.6899 | 94.0496 | 892.173 | 98.0801
7 | 674.417 | 95.8521 | 800.5275 | 86.272 | 900.7892 | 95.5451 | 816.9766 | 89.8134
8 | 709.6652 | 100.8617 | 892.9563 | 96.2329 | 913.3219 | 96.8744 | 875.7238 | 96.2717
9 | 678.3334 | 96.4087 | 941.5205 | 101.4666 | 935.2542 | 99.2007 | 814.6268 | 89.5551
10 | 799.5121 | 113.6313 | 1033.3401 | 111.3619 | 1028.8434 | 109.1276 | 1002.7626 | 110.2376

## Constants and Properties
Constants, Properties, Ratings, Pi Tags
Gas Properties to Cooler
Component | mole % | Cp at ~200 deg F | xi*Cp,i | Cp,mix [BTU/lb/°F] | Molar mass (lb/lb-mol) | xi*MM,i | MM, mix (lb/lb-mol)
Nitrogen | 2.325% | 0.24 | 0.00558 | 0.54368 | 28 | 0.651 | 25.4399
Methane | 60.04% | 0.552 | 0.33143 |  | 16.05 | 9.6367
Carbon Dioxde | 1.106% | 0.219 | 0.0024221 |  | 44 | 0.48664
Ethane | 19.73% | 0.584 | 0.1152 |  | 30 | 5.9178
Propane | 9.954% | 0.533 | 0.053055 |  | 44.1 | 4.3897
i-Butane | 1.141% | 0.535 | 0.0061044 |  | 58.124 | 0.66319
n-Butane | 3.507% | 0.518 | 0.018166 |  | 58.124 | 2.0384
i-Pentane | 0.71% | 0.567 | 0.0040257 |  | 72.151 | 0.51227
n-Pentane | 1.092% | 0.522 | 0.0057002 |  | 72.151 | 0.78789
n-Hexane | 0.309% | 0.505 | 0.0015604 |  | 86.18 | 0.2663
n-Heptane | 0.075% | 0.497 | 0.00037275 |  | 100 | 0.075
n-Octane | 0.012% | 0.492 | 5.904e-05 |  | 114.232 | 0.013708
n-Nonane | 0.001% | 0.487 | 4.87e-06 |  | 128.26 | 0.0012826
n-Decane | 0 | 0.483 | 0 |  | 142 | 0
Rated Duty (1000 BTU/hr) - Taken After Cleaning
Cooler type | IC-1 | IC-2 | IC-3 | AC
156EF-R-112-26 | 703.602 | 927.9115 | 942.7898 | 909.6375
Relevant Pi Tags
Cooler # | IC-1 |  | IC-2 |  | IC-3 |  | AC/IC-4 |  | FIT
| T_in | T_out | T_in | T_out | T_in | T_out | T_in | T_out | -
1 | 792108 | 792112 | 792109 | 792113 | 792110 | 792114 | 792111 | 792115 | 792120
2 | 792208 | 792212 | 792209 | 792213 | 792210 | 792214 | 792211 | 792215 | 792220
3 | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦
4 | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦
5 | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦
6 | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦
7 | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦
8 | V | V | V | V | V | V | V | V | V
9 | 792908 | 792912 | 792909 | 792913 | 792910 | 792914 | 792911 | 792915 | 792920
10 | 792008 | 792012 | 792009 | 792013 | 792010 | 792014 | 792011 | 792015 | 792020
Rated Duty (1000 BTU/hr) - Spec Sheet
Cooler type | IC-1 | IC-2 | IC-3 | AC
156EF-R-112-26 | 935.2 | 1663.6 | 1831.6 | 2187.3
𝐶_(𝑝,𝑚𝑖𝑥)=∑_𝑖▒〖𝑥_𝑖 𝐶_(𝑝,𝑖) 〗
〖𝑀𝑀〗_𝑚𝑖𝑥=∑_𝑖▒〖𝑥_𝑖 〖𝑀𝑀〗_𝑖 〗

## Sheet1
Cooler 1 | IC-1 | IC-2 | IC-3 | IC-4 | Cooler 2 | IC-1 | IC-2 | IC-3 | IC-4 | Cooler 3 | IC-1 | IC-2 | IC-3 | IC-4 | Cooler 4 | IC-1 | IC-2 | IC-3 | IC-4 | Cooler 5 | IC-1 | IC-2 | IC-3 | IC-4 | Cooler 6 | IC-1 | IC-2 | IC-3 | IC-4 | Cooler 7 | IC-1 | IC-2 | IC-3 | IC-4 | Cooler 8 | IC-1 | IC-2 | IC-3 | IC-4 | Cooler 9 | IC-1 | IC-2 | IC-3 | IC-4 | Cooler 10 | IC-1 | IC-2 | IC-3 | IC-4
Timestamp | Duty | Duty | Duty | Duty | Timestamp | Duty | Duty | Duty | Duty | Timestamp | Duty | Duty | Duty | Duty | Timestamp | Duty | Duty | Duty | Duty | Timestamp | Duty | Duty | Duty | Duty | Timestamp | Duty | Duty | Duty | Duty | Timestamp | Duty | Duty | Duty | Duty | Timestamp | Duty | Duty | Duty | Duty | Timestamp | Duty | Duty | Duty | Duty | Timestamp | Duty | Duty | Duty | Duty
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!