## Inlet coolers (5)
HGF Inlet Cooler (5) Efficiency Calculator
Temperatures (°F) | [13 empty] | Date of Assess
Cooler # | IC-1 |  | IC-2 |  | IC-3 |  | AC/IC-4 |  | EJW |  | TAW/CLO |  |  | 2025-06-26
| T_in | T_out | T_in | T_out | T_in | T_out | T_in | T_out | T_in | T_out | T_in | T_out
1 | 226.3333 | 128.5 | 204 | 123.4 | 216 | 123.3 | 220 | 125.2 | 181
2 | 237 | 117.9 | 199 | 117.4 | 212 | 117.6 | 226 | 116 | 181
3 | 245 | 108.7 | 195 | 114 | 207 | 112.4 | 219 | 120.3 | 181
4 | 194 | 117.3 | 210 | 116.8 | 245 | 114.7 | 229 | 116 | 181
5 | 201 | 102.8 | 203 | 101 | 239 | 105.6 | 233 | 115.9 | 174
Flows (MMCFD) |  |  |  | T Setpoint (°F) & Louver Position (%)
Cooler # | Inlet Gas Today | Total Flow Today |  | Cooler # | IC-1 |  |  | IC-2 |  |  | IC-3 |  |  | AC/IC-4
1 | 12.6158 | 12.7289 |  |  | T Setpoint | Louver | Actual T | T Setpoint | Louver | Actual T | T Setpoint | Louver | Actual T | T Setpoint | Louver | Actual T
2 | 11.8932 | 12.0011 |  | 1 | 120 | 17.9% | 128.5 | 123.4 | 67.8% | 123.4 | 120 | 27.8% | 123.3 | 120 | 27.5% | 125.2
3 | 11.1843 | 11.2738 |  | 2 | 120 | 19.1% | 117.9 | 120 | 7.5% | 117.4 | 120 | 67.1% | 117.6 | 120 | 29.3% | 116
4 | 6.4254 | 6.4342 |  | 3 | 120 | 32.8% | 108.7 | 120 | 12% | 114 | 120 | 25.4% | 112.4 | 120 | 43.3% | 120.3
5 | 6.525 | 6.5789 |  | 4 | 120 | 42.6% | 117.3 | 120 | 24.7% | 116.8 | 120 | 57.2% | 114.7 | 120 | 9% | 116
|  |  |  | 5 | 100 | 47.1% | 102.8 | 100 | 26.7% | 101 | 105 | 40.1% | 105.6 | 115 | 35.8% | 115.9
Actual Duty (1000 BTU/hr)
Cooler # | IC-1 |  | IC-2 |  | IC-3 |  | AC/IC-4 |  | EJW |  | TAW
| Duty | Efficiency % | Duty | Efficiency % | Duty | Efficiency % | Duty | Efficiency % | Duty | Efficiency % | Duty | Efficiency %
1 | 1838.8104 | 88.6989 | 1514.9041 | 105.4488 | 1742.3277 | 104.7362 | 1781.7979 | 99.4529 | #REF! | #REF! |  | 0
2 | 2110.4314 | 101.8011 | 1445.9379 | 100.6482 | 1672.7517 | 100.5538 | 1949.181 | 108.7955 |  | 0 |  | 0
3 | 2270.0397 | 109.5001 | 1349.0331 | 93.9029 | 1575.5375 | 94.71 | 1643.8219 | 91.7516 |  | 0 |  | 0
4 | 731.4534 | 86.7816 | 888.8064 | 94.5532 | 1242.6124 | 97.8837 | 1077.6301 | 97.2777 |  | 0 |  | 0
5 | 954.2799 | 113.2184 | 991.2072 | 105.4468 | 1296.3436 | 102.1163 | 1137.9448 | 102.7223 |  | 0 |  | 0

## FG coolers (3)
HGF Flash Gas Cooler (3) Efficiency Calculator
Temperatures (°F) | [7 empty] | Date of Assess
Cooler # | AC |  | EJW |  | TAW/CLO |  |  | 2025-06-30
| T_in | T_out | T_in | T_out | T_in | T_out
1 | 189 | 108 | 190 | 122
2
3
Flows (MMCFD) |  |  |  | T Setpoint (°F) & Louver Position (%)
Cooler # | Inlet Gas Today | Total Flow Today |  | Cooler # | AC |  |  | EJW |  |  | TAW
1 | 14.134 |  |  |  | T Setpoint | Louver | Actual T | T Setpoint | Louver | Actual T | T Setpoint | Louver | Actual T
2 |  |  |  | 1
3 |  |  |  | 2
3
Actual Duty (1000 BTU/hr)
Cooler # | AC |  | EJW |  | TAW
| Duty | Efficiency % | Duty | Efficiency % | Duty | Efficiency %
1 | 1698.024 | 100 |  | 0 |  | 0
2 | #DIV/0! | #DIV/0! |  | 0 |  | 0
3 | #DIV/0! | #DIV/0! |  | 0 |  | 0

## Refrig coolers (2)
HGF Refrig Cooler (2) Efficiency Calculator
Temperatures (°F) | [7 empty] | Date of Assess
Cooler # | EJW |  | TAW |  |  |  |  | 2025-06-30
| T_in | T_out | T_in | T_out
1 | 192 | 121
2
Flows (MMCFD) |  |  | T Setpoint (°F) & Louver Position (%)
Cooler # | Inlet Gas Today |  | Cooler # | EJW |  |  | TAW
1 |  |  |  | T Setpoint | Louver | Actual T | T Setpoint | Louver | Actual T
2 |  |  | 1
2
Actual Duty (1000 BTU/hr)
Cooler # | EJW |  | TAW
| Duty | Efficiency % | Duty | Efficiency %
1 | #DIV/0! | #DIV/0! | #REF! | #REF!
2 | #DIV/0! | #DIV/0! |  | 0

## Constants and Properties
Constants, Properties, Ratings, Pi Tags
Gas Properties to Cooler
Component | mole % | Cp at ~200 deg F | xi*Cp,i | Cp,mix [BTU/lb/°F] | Molar mass (lb/lb-mol) | xi*MM,i | MM, mix (lb/lb-mol)
Nitrogen | 0.02249 | 0.24 | 0.0053976 | 0.54375 | 28 | 0.62972 | 26.0088
Methane | 0.59446 | 0.552 | 0.32814 |  | 16.05 | 9.5411
Carbon Dioxde | 0.00997 | 0.219 | 0.0021834 |  | 44 | 0.43868
Ethane | 0.19135 | 0.584 | 0.11175 |  | 30 | 5.7405
Propane | 0.10028 | 0.533 | 0.053449 |  | 44.1 | 4.4223
i-Butane | 0.01257 | 0.535 | 0.006725 |  | 58.124 | 0.73062
n-Butane | 0.03955 | 0.518 | 0.020487 |  | 58.124 | 2.2988
i-Pentane | 0.00915 | 0.567 | 0.005188 |  | 72.151 | 0.66018
n-Pentane | 0.01482 | 0.522 | 0.007736 |  | 72.151 | 1.0693
n-Hexane | 0.00437 | 0.505 | 0.0022068 |  | 86.18 | 0.37661
n-Heptane | 0.00086 | 0.497 | 0.00042742 |  | 100 | 0.086
n-Octane | 0.00012 | 0.492 | 5.904e-05 |  | 114.232 | 0.013708
n-Nonane | 1e-05 | 0.487 | 4.87e-06 |  | 128.26 | 0.0012826
n-Decane | 0 | 0.483 | 0 |  | 142 | 0
Rated Duty (1000 BTU/hr) - Inlet Coolers
Cooler type | IC-1 | IC-2 | IC-3 | AC | EJW | TAW/CLO
H156-3-60 | 2073.0938 | 1436.6251 | 1663.5389 | 1791.6002 | 2654 | 4139.3
H156-2-44 | 842.8666 | 940.0068 | 1269.478 | 1107.7874 | 1305.8 | 2101.6 |  |  |  | Rated Duty (1000 BTU/hr) - Inlet Coolers - Spec Sheet
[10 empty] | Cooler type | IC-1 | IC-2 | IC-3 | AC | EJW | TAW/CLO
Relevant Pi Tags - Inlet Coolers | [9 empty] | H156-3-60 | 3050 | 2516 | 2958 | 4103 | 2654 | 4139.3
Cooler # | IC-1 |  | IC-2 |  | IC-3 |  | AC/IC-4 |  | FIT | H156-2-44 | 1050.1 | 1270.6 | 1561 | 2433.5 | 1305.8 | 2101.6
| T_in | T_out | T_in | T_out | T_in | T_out | T_in | T_out | -
1 | Compressor discharge temp (From Op Rounds) | 752111 | From Op Rounds | 752112 | From Op Rounds | 752113 | From Op Rounds | 752114 | 752101 | Rated Duty (1000 BTU/hr) - FG Coolers - Spec Sheet
2 | ¦ | 752211 | ¦ | 752212 | ¦ | 752213 | ¦ | 752214 | 752201 | Cooler type | AC | EJW | TAW
3 | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | H120-1-16 | 2431.6 | 187.07 | 136.11
4 | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦ | ¦
5 | V | V | V | V | V | V | V | V | V | Rated Duty (1000 BTU/hr) - Refrig Coolers - Spec Sheet
[10 empty] | Cooler type | EJW | TAW
Rated Duty (1000 BTU/hr) - FG Coolers | [9 empty] | H90-1-12 | 2971.3 | 395.9
Cooler type | AC | EJW | TAW
H120-1-16 | 1698.024 | 187.07 | 136.11
Relevant Pi Tags - FG Coolers
Cooler # | AC |  | EJW |  | TAW |  | FIT
| T_in | T_out | T_in | T_out | T_in | T_out | -
1 | Cylinder outlet temps (from operator rounds) | 758113 | From Op Rounds | From Op Rounds | ? | ? | 758111
2
3
Rated Duty (1000 BTU/hr) - Refrig Coolers
Cooler type | EJW | TAW
H90-1-12 | 2971.3 | 395.9
Relevant Pi Tags - Refrig Coolers
Cooler # | EJW |  | TAW
| T_in | T_out | T_in | T_out
1 | From Op Rounds | From Op Rounds | ? | ?
2
𝐶_(𝑝,𝑚𝑖𝑥)=∑_𝑖▒〖𝑥_𝑖 𝐶_(𝑝,𝑖) 〗
〖𝑀𝑀〗_𝑚𝑖𝑥=∑_𝑖▒〖𝑥_𝑖 〖𝑀𝑀〗_𝑖 〗